## Sheet1
Infection Control Risk Assessment (ICRA)
Name of Project: |  | 0 |  | Project #: | 0
Location of Construction: |  | 0 |  | Project Start Date: | 0
Phasing?: |  | Yes No | How Many?: | Estimated Duration / Project End Date: | 0 | 0
Patient Relocation?: |  | Yes No |  | Contractor: | 0
Relocation area: |  |  |  | IP Representative: | 0
Facility EH&S Representative: |  | 0 |  | Facility Representative: | 0
CONSTRUCTION ACTIVITY TYPES: Mark "X" in box under type
Work Type A | Inspection and non-invasive activities, involving no dust, including but is not limited to:
· Painting (but not sanding)
· Electrical trim work, , and activities which do not generate dust or require cutting of walls or access to ceiling other then for visual inspection
Work Type B | Small scale, short duration activities which create minimal dust, including but not limited to:
· Minor plumbing
· Removal of ceiling tiles for visual inspection
· Installation of telephone and computer cabling using existing "J" hooks or wire trays
· Removal of < or = to 5 floor tiles or carpet squares
· Access to chase spaces
· Cutting a small area of a wall where dust migration can be controlled such as within a closed chase space or use of a hepavac while cutting
Work Type C | Typically large scale, longer duration activity (e.g.> one work shift) that generates a moderate to high level of dust, requires demolition or removal of any fixed building components or assemblies, including but not limited to:
· Sanding walls
· Removal > 5 floor tiles or carpet squares or removal of casework
· Any work above ceilings including J Hook or wire tray installation
· Major cabling activities
· Major demolition
· Wall covering or cove base removal
· New construction
INFECTION CONTROL RISK GROUPS: Mark "X" in box next to group number. Using the following table, identify the patient risk group that will be affected. Consider impact on areas immediatley above, below and or adjacent to the area where the active work is being performed.
Patient/Location Group 1- |  |  |  | Patient/Location Group 2-
· Cardiology |  | · All inpatient areas EXCEPT adult & pediatric oncology, and bone marrow transplant |  | · Transplant units, including Bone Marrow Transplant Unit | · All laboratory areas
· Echocardiography |  |  |  | · Intensive Care Units | · Special Care Nurseries (level 2 or >)
· Endoscopy suites |  | · Emergency Department |  | · Interventional Radiology (Special Procedures) | · Dialysis Units
· Nuclear Medicine |  | · Labor and Delivery |  | · Central Sterile Processing | · Inpatient Oncology area
· Outpatient clinics, excluding cancer clinics, transplant clinincs and chemo infusion centers |  | · Well baby nurseries |  | · Operating Room (including C-section rooms) | · Pharmacy, main and all satelites
· Pulmonary function transplant clinics |  | · Pediatrics |  | · Cancer clinics, including chemo centers, transplant clinic | · Cardiac Cath Lab/Hybrid Ors
· Kitchen, cafeteria |  | · Pre and post op areas |  | · Radiation oncology/Gamma knife/Linear accelerator/Proton therapy
· Radiology/MRI, CT |  | · Pain Management Clinic
· Respiratory Therapy |  | · Therapy Services
· Wound center |  | · Ultrasound
· Admitting |  | · Main lobby areas and/or common hallways
· Offices (e.g. no patients present) |  | · Medical Office Building/Doctors' offices
Not Required for Project

## Sheet2
Instructions: Match the Infection Control Risk Group with the Construction Activity Type to determine the Project Class and highlight the box in yellow.
Construction Activity
Risk Level |  | Type A (no dust) | Type B (minimal dust) | Type C (moderate / major dust)
Group 1 - |  | GREEN | YELLOW | RED
Group 2 - highest group for risk |  | GREEN | RED | RED
Job Class | Check if applicable | DURING Construction Project
GREEN |  | Interventions: |  | Additional Notes
No dust |  | Close doors to patient rooms or offices near work
Noninvasive |  | Doors closed to supply areas or cover clean supplies tightly; store supplies away from where work is performed
Inspection activities |  | Linen carts covered or moved away from where work is performed
Cover office furniture, counters and equipment with plastic; protect personal belongings as appropriate
Additional requirements not already documented: Obtain BAP
YELLOW (in addition to Green above) |  | Interventions: |  | Additional Notes
Small amount of dust in controlled environment |  | Infection Prevention Specialist consulted at least 3 business days (72 hrs) prior to start of project.
Post signage at beginning of project if project to last > 24 hours; Responsible persons: ____________________________________
Project superintendant or HSO specific Facilities worker to check in with department manager or designee (e.g. charge nurse) at the beginning of each shift : _______Charge nurse _______Department / Office manager ________Other (specify)
Use methods to minimize migration of dust, other contaminants and or aerosolization of water, such as working within a cube, misting of ceiling surface with water (with or without bleach), appropriate plastic barrier, use of hepavac while cutting, etc.
Mist carpet tiles before removal
No patients present in active work area
Materials being brought to project site should be covered/wrapped
Debris removed in covered containers
Designate an elevator or route for debris removal when necessary
Open penetrations must be covered if unattended (e.g. plastic, dry wall, etc)
Access panels without barriers must be closed if unattended
Ceiling tiles replaced ASAP and must be closed if unattended
Walk off sticky mats
Clean work site at end of workday.
HEPA machine in area as air scrubber. Designate location of machine: __________________________
Additional requirements not already documented: Obtain BAP
RED (in addition to Green+Yellow above) |  | Interventions: |  | Additional Notes
Patients to wear masks when entering or leaving HSO. Notification responsibility person: ____IP ______Other (Specify)
Barriers constructed and inspected by IP prior to beginning work
Barrier type: ____Air tight soft (plastic) wall (acceptable if work lasts 72-96 hrs or less per discretion of IP/Safety); ____ Airtight hard wall partition (floor to deck); _______Airtight hard wall partition (floor to ceiling)
Ceiling plastic curtain required
Barrier seams taped
Maintain negative air flow within constuction site (Note: cap off air supply if necessary to achieve negative pressure)
Check pre filters on fans or units used to maintain negative airflow (commonly HEPA) at least daily or more frequently if major demolition
Use visual monitor/aide for negative air pressure.
Contractor to document at least daily that negative pressure is being maintained.
Return air vents blocked or sealed before beginning work if applicable.
Monitor and change return vent filters as needed and document.
Workers to remove dust from clothing prior to entering any hospital areas; e.g. sticky mats, vacuum clothing, apply clean clothing or remove coveralls and shoe coverings
When going thru sensitive areas, protective attire (PA) must be worn to access anteroom and work area. PA must be removed before entering the work area because it will be used again to exit through the sensitive area.
Keep work area clean e.g. wet mop or HEPA vac frequently ______X per day to decrease risk of tracking dust through clean areas
Wet mat (may consider 10% bleach solution); If using both sticky mas and wet mats, order should be wet mat, dry mat, sticky mat)
Create an ante room (ORs, hemonc/BMT units, large areas where negative pressure difficult to achieve, etc)
Mist outdoor construction site frequently and as needed to prevent dust aerosolization
Wet cut cement
Assess location of air intakes for outdoor projects and/or projects where work is being done < 75 ft from intakes- additional or higher filtration may be requried to avoid entry of contamination (e.g. dust and debris) of air intakes
Partner with EH&S to determine if air sampling (e.g. particle counts) is required during the project.
Additional requirements not already documented: Obtain BAP
Not Required for Project