Annual Inspection of Swinging Fire Door Assemblies

Fire Door Assembly Location: ___________________________________________________________

Special Locking Arrangement?: __________________________________________________________

Number of Leafs: _________ Fire Rating of Each Leaf: _____________ Fire Rating of Frame: ________

Rating of Barrier: ___________         Automatic or Manual Operator? _____________________

Hold-open Device? ____________________

Inspected By: __________________________________________ Date: _________________________

| Inspection Activity: | Yes | No | N/A | Comments |
| --- | --- | --- | --- | --- |
| - Is the door and frame free from holes and breaks in all surfaces? |  |  |  |  |
| - Are all the glazing, vision light frames and glazing beads intact and securely fastened? |  |  |  |  |
| - Are the doors, hinges, frame, hardware and threshold secure, aligned and in working order with no visible signs of damage? |  |  |  |  |
| - Is the door free of any missing or broken parts? |  |  |  |  |
| - Is the clearance from the door edge to the frame no more than 1/8 inch? |  |  |  |  |
| - Is the door undercut no more than ¾ inch? |  |  |  |  |
| - Does the active door leaf completely close when operated from the full open position? |  |  |  |  |
| - Does the inactive leaf close before the active leaf when a coordinator is used? |  |  |  |  |
| - Does the latching hardware operate and secure the door in the closed position? |  |  |  |  |
| - Is the door assembly free from any auxiliary hardware items which could interfere with its operation? |  |  |  |  |
| - Is the door free of modifications since original installation? |  |  |  |  |
| - If gasketing and edge seals are installed, have they been verified for integrity and operation? |  |  |  |  |

All “No” answers must be fully explained.				            Source: NFPA 80, 2010 edition

Supervisor’s Initial: _________ Date: __________________ Work Order #: _______________________